## Sheet1
Location : | In the Cavern (near the detector) |  |  |  | Cables |  | In the Counting house
| Analog front-end (PS in the counting) | L0 front end included in the Analog... (PS in the counting) | ECS | Regulators (PS in the counting) | Lost in the Cables |  | L1 front-end | PS for the L1 FE | HV | PS for the FE in cavern
Outer Tracker | Analog front-end | L0 front end |  |  |  |  | L1 front-end
Power consumption of chip [W] | 0.5 | 0.5 | [5 empty] | 75% efficiency |  | 75% efficiency
Number of chips per board | 2 | 4 OTIS 1 GOL
Power consumption of board [W] | 1 | 3 |  |  |  |  | 100 | 2.7 |  | 19.4
Number of boards | 3456 | 426 |  |  |  |  | 27 | 25% |  | 25%
Total power consumption of boards [kW] | 3.5 | 1.3 | 0.4 | 4.8 | 9.4 |  | 2.7 | 0.7 | 1.5 | 4.9
Cooled ? | yes | yes | yes | yes | no |  | yes | yes | yes | yes
Inefficiency % | 15% | 15% | 5% | 15% | 100% |  | 5% | 5% | 5% | 5%
cavern (detector) / counting house part % |  |  |  |  | 90% | 10%
heat dissipated to air [kW] | 0.525 | 0.195 | 0.02 | 0.72 | 8.46 | 0.94 | 0.135 | 0.035 | 0.075 | 0.245
heat removed by the cooling system [kW] | 2.975 | 1.105 | 0.38 | 4.08 | 0 | 0 | 2.565 | 0.665 | 1.425 | 4.655
Total power dissipated to air [kW] | 9.92 |  |  |  |  | 1.43
Total power to be cooled with water [kW] | 8.54 |  |  |  |  | 9.31
Total power consumption [kW] | 0 | [5 empty] | 29.2
|  |  |  | needed in the counting house |  |  | needed in the cavern but supplied from the counting house
Not sure, to be confirmed
Big dissipation to the air ! |  |  | Total: |  | 29.2 | kW | 0 | kW
|  |  | Total power needs: |  |  | 30 | kW
What still is missing or has to be confirmed: |  |  | Other sub-system that need power.…? Pumps, motors, etc…?
To dimension what TS-EL will have to provide to the sub-detectors in terms of electrical power, a 30% safety (or spare) margin should be added (in addition to what is still missing).