## Sheet1
Location : | In the Cavern (near the detector) | [5 empty] | Cables |  | In the Counting house
| L0 front-end |  | ECS | Regulators for L0 FE |  | LVPS | Lost in the LV Cables per Repeater board |  | L1 front-end |  |  | LVPS for L1 | HVPS | PS
Rich 1 & 2 | L0 front-end RICH 1 | L0 front-end RICH 2 |  | for Rich 1 | for Rich 2 |  |  |  | L1 front-end RICH 1 (throttle or included) | L1 front-end RICH 2 (throttle or included) | regulators |  |  | PS for other electronics, sub-systems, spare
Power consumption of chip [W] | [5 empty] | with 75% efficiency | [5 empty] | with 75% efficiency
Number of chips per board | 2 Pixel 2 PINT 2Analog pilot 4 GOL | 2 Pixel 2 PINT 2Analog pilot 4 GOL
Power consumption of board [W] | 11 | 11 |  | 8.5 | 8.5 | 6.1 |  |  | 120 | 120 |  | 1.4
Number of boards | 98 | 144 |  | 98 | 144 | 75% |  |  | 5 | 6 | already included | 75%
Total power consumption of boards [kW] | 1.1 | 1.6 | 0.2 | 0.9 | 1.3 | 2.1 | 1 |  | 0.6 | 0.8 |  | 0.5 | 1 | 2
Cooled ? | ? | ? | ? |  |  | yes | no |  | yes | yes |  | yes | yes | yes
Inefficiency % | ? | ? | ? |  |  | 10% | 100% |  | 5% | 5% |  | 5% | 5% | 5%
cavern (detector) / counting house part % | [6 empty] | ? | ?
heat dissipated to air [kW] | #VALUE! | #VALUE! | #VALUE! |  |  | 0.13 | ? | ? | 0.03 | 0.04 |  | 0.025 | 0.05 | 0.1
heat removed by the cooling system [kW] | #VALUE! | #VALUE! | #VALUE! |  |  | 1.17 | 0 | 0 | 0.57 | 0.76 |  | 0.475 | 0.95 | 1.9
Total power dissipated to air [kW] | ? | [6 empty] | 0.3
Total power to be cooled with water [kW] | ? | [6 empty] | 4.7
Total power consumption [kW] | 8.2 | [7 empty] | 4.9 | [5 empty] | 14 | kW
[7 empty] | needed in the cavern but supplied from near the counting house |  |  |  | needed in the counting house
Not sure, to be confirmed
Big dissipation to the air ! |  | Total: | For the RICH 1 |  |  |  | 3.7 | kW |  |  | 2.4 | kW
|  |  | For the RICH 2 |  |  |  | 4.6 | kW |  |  | 2.6 | kW
[7 empty] | 8.3 |  |  |  | 5
What still is missing or has to be confirmed: |  |  | Other sub-system that need power.…? Pumps, motors, etc…?
To dimension what TS-EL will have to provide to the sub-detectors in terms of electrical power, a 30% safety (or spare) margin should be added (in addition to what is still missing).