## Sheet1
Location : | In the Cavern (near the detector) but Powered from the counting house |  | Cables |  | In the Counting house
| Detector hybrid + Service boxes |  | Lost power in the cables |  | PS for the FE in cavern | L1 front-end | PS for the L1 FE | HV power on detector | HV power supplies
Trigger Tracker | Regulators included |  |  |  |  | L1 front-end
Power consumption of chip [W] |  |  |  |  | 75% efficiency |  | 75% efficiency |  | 20% efficiency
Number of chips per board
Power consumption of board [W] |  |  |  |  | 5.8 | 100 | 4.7 | 3.2 | 1
Number of boards |  |  |  |  | 75% | 47 | 75% | 296 | 20%
Total power consumption [kW] | 4.4 |  | 1.4 |  | 2 | 4.7 | 1.6 | 1 | 4
Cooled ? | yes |  | no |  | yes | yes | yes | yes | yes
Inefficiency % | 15% |  | 100% |  | 5% | 5% | 5% | 15% | 5%
cavern (detector) / counting house part % |  |  | 90% | 10%
heat dissipated to air [kW] | 0.66 |  | 1.26 | 0.14 | 0.2 | 0.235 | 0 | 0.15 | 0.2
heat removed by the cooling system [kW] | 3.74 |  | 0 | 0 | 3.8 | 4.465 | 0 | 0.85 | 3.8
Total power dissipated to air [kW] | 1.92 |  |  | 0.93
Total power to be cooled with water [kW] | 3.74 |  |  | 12.92
Total power consumption [kW] | [5 empty] | 19.1
|  |  |  | needed in the counting house |  |  | needed in the cavern but supplied from the counting house
Not sure, to be confirmed
Big dissipation to the air ! |  |  | Total: |  | 11.3 | kW | 7.8 | kW
|  |  | Total power needs: |  |  | 19.1 | kW
What still is missing or has to be confirmed: |  | Other sub-system that need power.…? Pumps, motors, etc…?
To dimension what TS-EL will have to provide to the sub-detectors in terms of electrical power, a 30% safety (or spare) margin should be added (in addition to what is still missing).