## Sheet1
Location : | In the Cavern (near the detector) | [5 empty] | Cables |  | In the Counting house
| L0 front-end |  |  | ECS | LVPS for L0 FE | Vacuum system | Lost in the LV Cables per Repeater board |  | L1 front-end |  | PS for L1 FE | HV | PS for other equipment, spares, etc.
VELO | L0 front-end (hybrid) | Repeater board, regulators included | regulators |  | 75% efficiency |  |  |  | L1 front-end | Regulators
Power consumption of chip [W] | 1 | [9 empty] | 75% efficiency
Number of chips per board | 16
Power consumption per board [W] | 16 | 22 |  | 100 | 4.7 |  | 12 |  | 100 |  | 25%
Number of boards | 88 | 88 | already included | 1 | 25% |  | 88 |  | 84 | already included | 9
Total power consumption [kW] | 1.5 | 2 |  | 0.1 | 1.2 | 2.5 | 1.1 |  | 9 |  | 3 | 1
Cooled ? | ? | ? |  | no | yes | ? | no |  | yes |  | yes | yes
Inefficiency % | ? | ? |  | 100% | 5% | ? | 100% |  | 5% |  | 5% | 5%
cavern (detector) / counting house part % | [6 empty] | 90% | 10%
heat dissipated to air [kW] | #VALUE! | #VALUE! |  | 0.1 | 0.06 | #VALUE! | 0.99 | 0.11 | 0.45 |  | 0.15 | 0.05
heat removed by the cooling system [kW] | #VALUE! | #VALUE! |  | 0 | 1.14 | #VALUE! | 0 | 0 | 8.55 |  | 2.85 | 0.95
Total power dissipated to air [kW] | #VALUE! | [6 empty] | 0.76
Total power to be cooled with water [kW] | #VALUE! | [6 empty] | 12.35
Total electrical power consumption [kW] | 0 | [7 empty] | 22
[7 empty] | needed in the counting house |  |  | needed in the cavern but supplied from the counting house
Not sure, to be confirmed
Big dissipation to the air ! | [5 empty] | Total: |  | 13 | kW | 9 | kW
[6 empty] | Total power needs: |  |  | 22 | kW
What still is missing or has to be confirmed: |  |  |  | Other sub-system that need power.…? Pumps, motors, etc…?
To dimension what TS-EL will have to provide to the sub-detectors in terms of electrical power, a 30% safety (or spare) margin should be added (in addition to what is still missing).