## Sheet1
Location : | In the Cavern (near the detector) | [5 empty] | Cables |  | In the Counting house
| L0 front-end |  | ECS | L0 trigger |  |  | Lost in the LV Cables per Repeater board |  | L1 front-end | L0 trigger | PS for L1 FE and L0 trigger | HV | PS for the front-end in cavern
Pile up VETO | L0 front-end | Repeater boards, regulators included |  | Service box | Optical station | PS for the L0 service box |  |  | L1 front-end / TELL 1 | Trigger
Power consumption of chip [W] | 1 |  |  |  |  | 75% efficiency |  |  |  |  | 75% efficiency |  | 75% efficiency
Number of chips per board | 16
Power consumption per board [W] | 16 | 42 |  |  |  | 0.6 | 56.2 |  | 100 |  | 1 |  | 0.7
Number of boards | 4 | 4 |  |  |  | 25% | 4 |  | 4 |  | 25% |  | 25%
Total power consumption [kW] | 0.1 | 0.2 | 0.1 | 0.4 | 0.2 | 0.15 | 0.3 |  | 0.4 | 0.6 | 0.25 | 0.04 | 0.175
Cooled ? | yes | no | yes | no | no | yes | no |  | yes | yes | yes | yes | yes
Inefficiency % | 5% | 100% | 5% | 100% | 100% | 5% | 100% |  | 5% | 5% | 5% | 5% | 5%
cavern (detector) / counting house part % | [6 empty] | 90% | 10%
heat dissipated to air [kW] | 0.005 | 0.2 | 0.005 | 0.4 | 0.2 | 0.0075 | 0.27 | 0.03 | 0.02 | 0.03 | 0.0125 | 0.002 | 0.00875
heat removed by the cooling system [kW] | 0.095 | 0 | 0.095 | 0 | 0 | 0.1425 | 0 | 0 | 0.38 | 0.57 | 0.2375 | 0.038 | 0.16625
Total power dissipated to air [kW] | 1.09 | [6 empty] | 0.11
Total power to be cooled with water [kW] | 0.34 | [6 empty] | 1.4
Total electrical power consumption [kW] | 1 | [6 empty] | 0.3 | 1.465
[9 empty] | needed in the counting house |  |  | needed in the cavern but supplied from the counting house
Not sure, to be confirmed
Big dissipation to the air ! | [7 empty] | Total: |  | 1.8 | kW | 1 | kW
[8 empty] | Total power needs: |  |  | 3.5 | kW
What still is missing or has to be confirmed: |  |  |  |  | Other sub-system that need power.…? Pumps, motors, etc…?
To dimension what TS-EL will have to provide to the sub-detectors in terms of electrical power, a 30% safety (or spare) margin should be added (in addition to what is still missing).