## Sheet1
LHCb Cooling Matrix
|  |  | equipment | cooling agent | cooling capacity | temperature | comments
| Sub system |  |  |  | [W] | [ºC]
DT = 25ºC , DP = 10 bar, flow 150 m3/h
| Magnet |  | Coil | demineralised water | 5 x 106
| Vertex Locator |  | Hybrid | CO2 (R774) | 2.5 x 103 | range: -25 - 10 | two phase cooling system, 15 bar- 57 bar
| Inner Tracker |  | Hybrid | C6F14 | 2.45 x 103 | min -30 | alternativ: CO2 two phase
| Outer Tracker |  | Electronics
| RICH 1 |  | Electronics
| RICH 2 |  | Electronics
Calorimeter
SPD/PS
|  | Electromagnetic Calorimeter | PMP+base | air? water ? | 3.8 x103 |  | 2.5W per channel, 'inner region' high density: 9 PM's x 167 modules = 1503 channels on a surface of 1940mmx1454mm.
Hadron Calorimeter
Muon system
MultiWireProportionalChamber
ResistivePlateChamber
Counting House
D1
|  | Racks |  | Mixed water
|  | Room |  | Chilled Water
D2
|  | Racks |  | Mixed water
|  | Room |  | Chilled water
A
|  | Racks |  | Mixed water
|  | Room |  | Chilled water
B
|  | Racks |  | Mixed water
|  | Room |  | Chilled water
| Experimental Cavern | Air condition
Air condition
| Counting House Area | Air condition
| Control Room | Air condition
| Computer Farm | Air condition or Rack cooling | PC | Chilled water/Mixed water

## Sheet2
Electricity/Heat dissipation in the UX cavern | [12 empty] | 27-03-2003
|  | all numbers are given in kW | [14 empty] | cooled by
| Item | [11 empty] | Sum | power cooled by water | heat dissipated to air inside the barrack (cooled by the air cond) | heat dissipation to air | Mixed water | Chilled water | Deminerilzed water
Counting house
|  | D1 |  | D2 | A/B (D3)
| Electronics in Racks (5% inefficiency) |  |  | 203 | 236 | [7 empty] | 439 | 439 | 21.95 | 0 | x | x
| Electronics not in racks (PCs and others, during comissioning for example) | 2 |  | 2 | 2 | [7 empty] | 6 |  | 6 | 0 |  | x
| Light | 1 |  | 1 | 1 | [7 empty] | 3 |  | 3 | 0 |  | x
| People (100 W / person if 10 --> 1kW) | [9 empty] | 1 |  | 1 |  | 1 | 0
| General Service | [11 empty] | ? |  | 0 | 0 |  | x
| Farm (5% inefficiency) | 574 |  | 280 | [8 empty] | 854 | 854 | 42.7 | 0 | x | x
| Total in the counting houses | [13 empty] | 74.65
Counting House area
|  | Gas plat 86 |  | Gas plat 84 | DELPHI Barrel | Head wall
| Gas system | 2 |  | 2 | [8 empty] | 4 |  | 0 | 4
| Cooling system | 2 |  | 2 | [8 empty] | 4 |  | 0 | 4
| Air conditioning 18 kW consumption max per unit (estimate of kW dissipated) |  | ? | [11 empty] | 0 | ? |  |  |  | We don’t know what power is dissipated from the air conditionner units
| Exhibition (DELPHI) |  | 2 | [9 empty] | 2 |  | 0 | 2
| Magnet (MSS &MCS) |  |  |  |  | 1.5 | [6 empty] | 1.5 |  | 0 | 1.5
| Electronics close to PZ |  |  |  |  | ? | [8 empty] | 0 | ?
| SUM | [11 empty] | 1314.5 | 1293 | 74.65 | 11.5
Detector area
|  | VELO + VETO | IT + TT | RICH 1 + 2 |  | Magnet | OT | ECAL/HCALPS/SPD |  |  | Others | Muon
| Electronics in Racks (cooled, 5% inefficiency) | 1.6 | [5 empty] | 17.3 |  |  |  | 11.5 | 30.4 | 38 |  |  | x
| On-detector elec. (cooled, 15% inefficiency) |  | 3 |  |  |  | 8.5 | [5 empty] | 11.5 | 12 |  |  | x |  | x
| Service boxes (20% inefficiency) | [11 empty] | 0 | 0 |  |  | x
| On-detector electronics (s-box, cables...) not cooled so far | 12 | 7.23 | 2 |  |  | 8 | 2.7 |  |  |  | 10.5 |  |  |  | 42.43
| pumps, lights … | [9 empty] | 5 |  | 5 |  |  | 5
| Magnet |  |  |  |  | 8.5 | [6 empty] | 8.5 |  |  | 8.5
| Others | [11 empty] | 0 |  |  | ?
| SUM | 13.6 | 10.23 | 2 |  | 8.5 | 16.5 | 20 | 0 | 0 |  | 22 | 55.4 | 50 |  | 55.93
| TOTAL to be cooled by mixed water | [12 empty] | 1343
| Left cooling capacity by mixed water | [12 empty] | 157 | 1500 - the total power cooled by mixed water
| Not sure, to be confirmed |  |  | For the RICH it might be doubled !?
Big dissipation to the air !
Note on V28: Rolf Lindner: Outer Tracker
Note on I30: Bobillier Vincent: 7.7 Cables and 1.3 S-box

## Sheet3
Vertex |  | Quantitiy | dissipation | Sum | cooled by... water
[5 empty] | mixed | chilled | air
Repeater Board |  | 84
| Driver |  | 5 | 420
| Digital Part |  | 2 | 168
| Radhard regulators |  |  | 1000
Boards for Pil-up
| Repeater | 4 | 7 | 28
| Digital repeater | 16 | 5 | 80
Elec-to-opic station |  | 1 | 300 | 300
Ion-getter pump |  | 2 | 500 | 1000
Roughing pump, unidry |  | 3 | 1200 | 3600
Turbo pump |  | 4 | 100 | 400
60m cables |  |  |  | 1200
Hybrid |  |  |  | 2200 | 2200
|  |  |  | 10396 | 2200 | 0 | 8196
Calorimeter
PreShower/SPD
| PMs VFE | 12000 | 0.125 | 1500
| Readout electronics crates | 8 | 800 | 6400 |  | 5120
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
0
|  |  |  | 7900 |  | 5120 | 2780
Electromagentic Calorimeter | [5 empty] | 0
| PMs | 6000 | 0.25 | 1500 |  | 0
| Readout electronics crates | 14 | 800 | 11200 |  | 8960
|  |  |  | 12700 |  | 8960 | 3740
Hadronic Calorimeter | [5 empty] | 0
| PMs | 1500 | 0.25 | 375
| Readout electronics crates | 4 | 800 | 3200 |  | 2560
|  |  |  | 3575 |  | 2560 | 1015