## Sheet1
Location : | In the Cavern (near the detector) | [6 empty] | Cables |  | In the Counting house
| On detector |  |  | Off detector |  |  |  | Lost in the LVPS Cables (380VDC for MARATON PS) |  | L1 front end |  | L0 Muon Trigger |  | HV
MUON | Front end boards | LV regulators | LV cables (~10m) | IM boards | ODE boards | SB boards | LVPS for IM, ODE and SB crates | lost in the cables : ~4% of total power (considering 4mm2 cables) |  | L1 front end | LVPS for L1 FE | Trigger boards | PS
Power consumption of chip [W] |  |  | (20% lost in cables considering 10 meters of 2mm2 cable and ~3A per cable) |  |  |  | 75% efficiency |  |  |  | 75% efficiency
Number of chips per board
Power consumption of board [W] | 1.2 | 30% | 20% | 15 | 50 | 5 | 75% | 28.4 |  | 100 | 75% | 100 | 75%
Number of boards | 7632 | 9.2 | 12 | 152 | 148 | 144 | 10.5 | 4% |  | 8 | 0.8 | 84 | 8.4
Total power consumption [kW] | 9.2 | 2.8 | 2.4 | 2.3 | 7.4 | 0.8 | 3.5 | 1.2 |  | 0.8 | 0.3 | 8.4 | 2.8 | 10.5
Cooled ? | no | no | no | yes | yes | yes | yes | no |  | yes | yes | yes | yes | yes
Inefficiency % | 100% | 100% | 100% | 5% | 5% | 5% | 5% | 100% |  | 5% | 5% | 5% | 5% | 5%
cavern (detector) / counting house part % | [7 empty] | 90% | 10%
heat dissipated to air [kW] | 9.2 | 2.8 | 2.4 | 0.115 | 0.37 | 0.04 | 0.175 | 1.08 | 0.12 | 0.04 | 0.015 | 0.42 | 0.14 | 0.525
heat removed by the cooling system [kW] | 0 | 0 | 0 | 2.185 | 7.03 | 0.76 | 3.325 | 0 | 0 | 0.76 | 0.285 | 7.98 | 2.66 | 9.975
Total power dissipated to air [kW] | 16.18 | [7 empty] | 1.26
Total power to be cooled with water [kW] | 13.3 | [7 empty] | 21.66
| 12 |  |  | 14
Total electrical power consumption [kW] | 29.6 | [8 empty] | 22.8
[5 empty] | needed in the counting house |  |  | needed in the cavern but supplied from the counting house
Not sure, to be confirmed
Big dissipation to the air ! |  |  |  | Total: |  | 22.8 | kW | 29.6 | kW
|  |  |  | Total power needs: |  |  |  | 53 | kW
What might be forgotten: | Other sub-system that need power.…? Pumps, motors, etc…?
To dimension what TS-EL will have to provide to the sub-detectors in terms of electrical power, a 30% safety (or spare) margin should be added (in addition to what is still missing).